HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00063709
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0010248
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0049534
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0001494
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0088146
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0037577
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.0030865
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.01264
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0033268
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00035019
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.017081
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.0011798
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00034042
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 7.1285e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 2.1988e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.0266e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 5.8771e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.9652e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.2975e-07
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.7134e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0001241
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00059981
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.8085e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.001067
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00045503
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00037375
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.0015306
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00040285
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 4.2405e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0020683
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0072663
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0019416
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00043478
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00024601
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00019293
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00035098
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00016979
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 7.1633e-07
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0004239
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00068867
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0033286
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 9.8408e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0058061
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0025251
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0020741
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0084936
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0022356
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00023532
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.011478
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0021045
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0001615
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0011586
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0011597
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 3.6801e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.022036
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0061772
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0012408
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.00052918
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00045589
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0011381
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00058894
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 2.4303e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0032156
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0088569
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00045383
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 6.3898e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0054829
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0087746
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.042411
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0012924
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.076252
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.032174
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.026427
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.10822
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.028484
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0029983
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.14624
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.011009
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 3.3957e-07
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00026827
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 6.1187e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 6.6085e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 2.4165e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.1664e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 7.4381e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 4.6055e-07
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.9478e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 8.698e-07
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0.00022203
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00048474
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 4.4518e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 8.7397e-07
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.2642e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.8799e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.0313e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.2093e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 5.3812e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 3.225e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 3.6887e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00021728
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 4.5601e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 3.947e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00018716
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00082686
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00017873
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 3.9777e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 4.4551e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 1.6014e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 4.6154e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.958e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.7821e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 7.5896e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.1768e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 0.00014532
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00032407
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 3.0854e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 5.7316e-07
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.7661e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.1126e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 7.2118e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.8771e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00012803
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 7.6727e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 8.7759e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00051693
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00010849
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 9.3905e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00044529
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00055412
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0015319
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 2.9084e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00036832
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.00012931
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00058888
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00034155
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 1.9522e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 7.9205e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 3.3714e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.0013396
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0027457
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00023115
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 2.4207e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.557e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00023882
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00081524
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.0694e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0013659
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00086734
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00099205
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0058434
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0012264
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00010615
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0050336
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0052833
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.10726
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.002568
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.02581
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0084246
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.11764
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.071264
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0042573
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.017798
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0079371
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.087612
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.18604
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.016092
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00020244
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.010498
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.028696
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.097959
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0038657
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.17203
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.10422
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.1192
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.70215
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.14736
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.012755
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.60484
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.3296
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.463e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0054017
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.0023665
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00019489
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00028196
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00016183
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00052181
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00091982
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0044458
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00011054
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0065216
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0033727
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.0027702
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.011344
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0029859
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.0003143
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.01533
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.0010865
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00047841
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 3.8338e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 5.5848e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.0047e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.311e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00011124
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00053768
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.3369e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00078877
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.0004079
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00033504
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.001372
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00036112
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.8013e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0018541
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00749
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0029846
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0002269
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0003149
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00017229
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00037571
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00067944
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.003284
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.706e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0045465
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0024913
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0020463
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0083798
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0022056
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00023217
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.011324
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0020202
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 8.4975e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00088078
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.00034178
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.023321
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0097065
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.00077126
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0011029
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00063221
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0025916
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0078348
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00042673
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 3.374e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0041404
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0073339
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.035447
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00087183
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.051438
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.026891
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.022088
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.090451
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.023807
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.002506
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.12223
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.010906
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.9e-07
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00018082
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 5.0623e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 6.608e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 1.4777e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.0937e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 7.4005e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 6.8645e-07
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.5539e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 5.5023e-07
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0.00019268
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00036694
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 3.519e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.1852e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.8381e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.9447e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.688e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.9017e-07
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 3.0713e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.7958e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.054e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00012099
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.5393e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.1979e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00010422
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0006668
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00012155
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 3.0172e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 4.4378e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 9.7781e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 4.0926e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.9048e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.6378e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 9.806e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.9354e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 0.0001274
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00024061
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 2.252e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 6.8874e-07
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.3675e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.1719e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.0004e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.645e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 7.3204e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 4.2561e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 4.868e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00028674
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 6.018e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 5.2089e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.000247
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00044473
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0012022
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 3.3155e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00030284
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 8.7547e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00051065
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00041128
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 3.4571e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 9.9037e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 2.0187e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00089484
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.002388
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00019452
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 2.5151e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.1209e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00013127
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0004481
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.0311e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00090385
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00047674
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00054529
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0032119
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0006741
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 5.8348e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0027668
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0041097
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.065345
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0018586
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.024476
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0052657
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.099304
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.062985
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.005546
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.022926
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0044865
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.066124
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.13138
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.012243
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00035514
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0058489
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.015284
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.052173
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0022714
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.10108
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.055508
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.063488
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.37396
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.078486
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0067934
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.32214
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.23703
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 8.1864e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.005065
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.0023545
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00029049
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00036968
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00010237
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00029383
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0005122
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0024756
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.3088e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0037222
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.001878
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.0015426
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0063171
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0016627
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00017502
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0085366
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00096344
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00046981
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 5.6744e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 7.2157e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.8306e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.5492e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.1708e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00029825
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.6441e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.000451
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00022626
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00018585
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00076106
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00020031
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.1086e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0010285
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.006495
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.003594
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00040182
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00039375
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00010316
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00022484
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00037346
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0018051
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.0994e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0030086
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0013694
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0011248
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.004606
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0012123
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00012761
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0062244
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0012307
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 6.1501e-05
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00083526
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.00021363
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.019687
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0085788
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0010047
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0014207
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00035736
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.001956
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0055328
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00032467
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 5.919e-06
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0023069
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.003906
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.018879
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00051227
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.030224
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.014322
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.011764
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.048174
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.01268
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0013347
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.0651
HFTD - Distribution | HFTD - Distribution - 2QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0078431
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 5.1638e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0016355
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0.00013847
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00065933
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.0029246
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0.00010164
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 9.4263e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 1.7652e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.042e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 7.546e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 7.9174e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 6.1538e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.0028e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 5.5739e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 5.46e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.0798e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.6977e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.2348e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0.00026082
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00078232
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 9.8227e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 3.1195e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.4591e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.999e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.7306e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.5167e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 6.7495e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.9051e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 3.3228e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00019572
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 4.1077e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 3.5555e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0001686
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0007923
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.0011009
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 8.4467e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.00042534
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.001786
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 6.2456e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 3.2443e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 5.9428e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 8.3161e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 3.7199e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.8026e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 2.2465e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 3.5307e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.8538e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00019076
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 7.1734e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 5.9554e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.0596e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 0.00020612
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00057616
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 7.3639e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.9278e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.8076e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.0369e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.9531e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.8616e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00017184
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 7.3975e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 8.4611e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00049839
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.0001046
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 9.0537e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00042932
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0007085
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0091073
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.0003876
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0041631
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.011516
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.00053548
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 3.1363e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00057044
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0011363
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00043503
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00038245
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00029487
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00050231
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 1.9488e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0019203
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00074895
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00059521
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0002413
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.0020669
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0042175
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00071452
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.00024071
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00010349
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00024282
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00082889
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.4795e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0019934
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00088187
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0010087
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0059413
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0012469
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00010793
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.005118
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0048371
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.9544
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.056329
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.57079
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 1.5806
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.082323
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.023771
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.31089
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.54489
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.19531
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.19394
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.1617
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.25786
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.010397
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.99384
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.33566
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.28393
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.11115
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.24131
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.62613
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.096775
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.033412
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.028708
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.066536
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.22713
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.012562
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.55903
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.24165
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.27639
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 1.628
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.34168
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.029575
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 1.4024
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.67411
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.2248e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0.00058449
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0.0020281
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0094563
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.0024008
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.0033504
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.0041728
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0089918
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00035057
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0079035
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.0038697
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.0015432
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0002269
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00055297
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00082856
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0040047
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00013864
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00818
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0030381
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.0024954
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.010219
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0026897
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00028312
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.013809
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0.00010226
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0.0003471
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.0019577
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00060164
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0.00060289
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0.00077438
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0016093
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 5.9271e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.0014037
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0.00067848
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0.00027518
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.8103e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.1574e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00010725
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0005184
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.7944e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.0010587
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00039327
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00032302
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.0013228
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00034817
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.6649e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0017876
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00053413
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.0018001
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.014453
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0038015
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0044451
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.0054918
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.012371
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00033664
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0076346
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.0038273
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.001486
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00024119
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0004544
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00069082
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.003339
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00011246
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0066353
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.002533
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0020806
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0085202
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0022425
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00023606
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.011514
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.017976
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0018639
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.019479
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.064126
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.00087647
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.00631
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.015292
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.10802
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.026602
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.035136
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.04694
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.098984
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0027994
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.061587
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.026736
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.011048
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0017317
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.007138
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.026369
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0025663
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00055687
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.011323
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.017005
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.082189
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0028332
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.16716
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.06235
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.051213
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.20972
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0552
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0058105
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.28341
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.022306
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.5948e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00019885
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 4.577e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00012704
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 3.493e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 4.2423e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 6.6066e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 3.3497e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 3.5316e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 3.698e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 4.8768e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 5.6865e-08
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.8233e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 8.515e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.423e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 4.035e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0.00014961
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.0002622
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 4.9253e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.9575e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.4615e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.9074e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.6993e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.534e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 6.8261e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.8718e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 3.2847e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00019348
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 4.0607e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 3.5148e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00016667
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00048827
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00014066
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 3.3012e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 8.5749e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 2.4521e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 2.618e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.6283e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.4206e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.4413e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.2652e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.7257e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.9458e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.042e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.0773e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 4.9248e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.4362e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 0.00010268
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00018847
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 3.2764e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.1892e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.6293e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.9719e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.7312e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.8231e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00017013
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 7.1614e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 8.1911e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00048248
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00010126
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 8.7647e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00041561
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00036691
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0010259
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 1.8215e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00054982
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.00020366
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 2.7068e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00033748
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00016155
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 2.7324e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 1.3966e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 2.6409e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 2.1248e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00010982
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 3.3219e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 7.2716e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.9078e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00074753
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0016366
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00022394
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.00014582
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0001051
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00024059
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00082128
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.6495e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.002069
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00087378
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0009994
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0058868
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0012355
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00010694
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.005071
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0030422
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.17003
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0037886
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.10261
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.039755
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0053382
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.15047
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.074368
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0072323
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.01045
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.018968
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0016091
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.069893
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.019765
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.043064
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.015835
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.1065
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.21716
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.029839
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.021536
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.02812
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.064603
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.22053
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0124
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.55182
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.23463
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.26836
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 1.5807
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.33175
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.028715
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 1.3616
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.39397
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.118e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0030594
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.0010657
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00014945
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00025076
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00043728
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 3.5765e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00040869
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00015843
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00012935
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.4684e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00055335
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00081908
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0039589
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00014022
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0082728
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0030033
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.0024669
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.010102
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0026589
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00027988
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.013651
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00061873
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00022976
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 3.1005e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 4.3611e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 7.8659e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 6.2214e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 7.6674e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.9106e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 2.2756e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 2.6569e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.0125e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00010383
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00050185
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.7765e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.0010481
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00038072
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00031271
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.0012806
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00033706
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.548e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0017305
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0042924
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0014117
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00031759
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.0002601
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00065038
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 3.6705e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00043662
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00016976
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00018154
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.907e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00046148
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00068448
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0033083
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00011673
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0068872
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0025098
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0020615
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0084419
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0022219
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00023389
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.011408
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0032024
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00012536
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0035016
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0016128
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 5.6834e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.029831
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.010129
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0013102
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0030336
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0072811
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00043327
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0043312
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0015743
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0016758
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00024671
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0031503
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0091454
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00079129
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00035893
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.011091
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.01651
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0798
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0027966
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.165
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.060538
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.049725
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.20363
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.053595
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0056416
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.27517
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.013036
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 4.1958e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00010247
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.5997e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 4.5269e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 6.6789e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 9.962e-08
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 3.6987e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 3.4914e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 2.5059e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 1.5534e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.1705e-08
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.1239e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.809e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0.00010983
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00021807
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 1.9445e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 9.0393e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.6673e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.0004e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.3656e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.0689e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 3.1456e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.4529e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.6617e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 9.7882e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.0543e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.7781e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 8.4317e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00025189
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 6.7411e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.5991e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 3.1224e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 4.4352e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 6.7378e-08
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.4577e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.4104e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 9.8497e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 5.8327e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 4.3949e-08
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.2918e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.0471e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 8.2108e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00014381
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 1.309e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 5.41e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.2284e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.0149e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.4645e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.7921e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 7.9749e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 3.686e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 4.2159e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00024833
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 5.2118e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 4.5112e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00021392
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00017651
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00077382
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 1.8883e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00032175
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 4.9008e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 1.1056e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00021527
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00021414
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 1.3301e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 1.281e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 9.6521e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 6.1797e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 1.6763e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00070515
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0015914
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00013568
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 8.3407e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.2481e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00015215
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0005194
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.6117e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0011622
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.0005526
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00063204
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0037229
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00078135
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 6.7631e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.003207
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0019683
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.074964
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0021667
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.036069
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0052846
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.00017052
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.07872
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.061441
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0046183
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.006021
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00045368
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.022122
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0042105
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.0717
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.145
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.014343
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00092922
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.015265
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.036487
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.12455
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0064956
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.28905
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.13251
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.15157
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.89277
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.18737
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.016218
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.76904
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.20937
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.8078e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0017128
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.0011108
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00010604
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00010533
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.0495e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00016268
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 5.2264e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00026653
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00041437
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0020028
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.4616e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0038123
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0015194
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.001248
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0051106
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0013451
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00014159
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0069062
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00034316
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00022812
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.1189e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 2.0106e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.0033e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.1581e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 9.904e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.4361e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.3442e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0002583
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.3275e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00049132
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00019595
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00016095
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00065911
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00017348
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.8261e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0008907
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.002738
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0018713
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0001546
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00023857
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 2.3771e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00024569
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 8.5662e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00027433
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00043288
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0020923
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.5571e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0038687
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0015872
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0013037
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0053389
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0014052
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00014792
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0072147
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0014119
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 7.1695e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0012309
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.00021439
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 1.8155e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.015606
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0083685
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.00083667
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0017478
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00017415
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0013709
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00033538
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0021209
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0061067
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00038035
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 1.5487e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0060208
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0093249
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.04507
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0014649
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.086431
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.034191
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.028084
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.11501
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.03027
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0031863
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.15541
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.006928
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.5149e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0001152
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.6919e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 3.3156e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 7.7931e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 5.1368e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 4.6142e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.9384e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 2.0999e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.101e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.0229e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 3.8505e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 4.4667e-09
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 6.8363e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00011645
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 1.4625e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 5.1477e-08
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.0531e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.0126e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.8701e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.2804e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 1.4598e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 7.3092e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 8.3601e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 4.9244e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.0335e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 8.9456e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 4.2419e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00024949
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 7.8636e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.8289e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 2.3686e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 5.3998e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 3.1234e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.7915e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 7.5352e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 7.9409e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 3.7164e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.8387e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.3751e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.5078e-08
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 4.5972e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 8.1345e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 9.751e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 4.2769e-08
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.024e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.0631e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.7284e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.2367e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 3.6654e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.8388e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.1032e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00012389
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.6e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.2505e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00010672
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00017564
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0013977
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 2.6972e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00028428
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0001186
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 7.1715e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00033213
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00012871
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 1.703e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.1421e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 6.1766e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 3.3872e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 4.6339e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00060133
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0010445
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00012031
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 4.5019e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.4654e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.7017e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00029704
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.4048e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00062512
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00031603
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00036147
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0021291
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00044685
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 3.8678e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0018341
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0024432
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.10132
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.002564
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.029401
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0077391
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.00058993
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.11121
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.042354
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0046138
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0028631
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.020363
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0091827
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.00011616
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.055254
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.10595
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.012389
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 4.1124e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0068759
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.017123
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.058452
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.002811
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.12509
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.062188
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.071129
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.41897
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.087931
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.007611
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.36091
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.22939
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.0835e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0021368
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00061673
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 8.8864e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 9.8718e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00014807
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 7.1643e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 4.0601e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00012874
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00020847
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0010076
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.9986e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0017692
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00076438
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00062785
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0025711
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00067672
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 7.1234e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0034745
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00042172
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00012187
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.7083e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.694e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.5606e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.3006e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 6.9671e-08
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.6448e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.6661e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00012886
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.8274e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00022582
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 9.7756e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 8.0295e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00032882
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 8.6545e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 9.11e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00044434
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0042244
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0011247
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00019794
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00028128
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00024557
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.0001731
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 1.1569e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00015215
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00024756
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0011966
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.5268e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0020808
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00090773
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0007456
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0030533
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00080364
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 8.4593e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0041261
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0019084
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 8.484e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0010033
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.00031397
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 6.2808e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.022047
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0057689
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.00083584
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.001099
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0012619
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00073142
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 4.5202e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0016345
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0044621
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00032854
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 6.8539e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0027119
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0043761
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.021151
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00063395
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.037403
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.016046
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.01318
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.053972
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.014206
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0014953
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.072935
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0075903
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.5769e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 4.9141e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.6117e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 5.2918e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 1.6885e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.1196e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.8016e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.7569e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 9.7027e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.138e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 4.7253e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00013032
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 8.3828e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 3.6369e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.3107e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.3157e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.4914e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.1825e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 9.7119e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 4.7785e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 5.4655e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 3.2193e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 6.7566e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 5.8483e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 2.7732e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00020588
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 3.5102e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.0382e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 3.5169e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 1.1336e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 7.9719e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 7.3378e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 7.0247e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.9205e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 4.1349e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 3.2756e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 9.2652e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 6.2845e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 2.2191e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.3383e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.3109e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.1302e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.5078e-07
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 2.451e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.2025e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.3754e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 8.1013e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.7003e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.4717e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 6.9786e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00014263
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00043473
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 1.5156e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00035188
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 1.782e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00016145
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00011969
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 1.4352e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 5.6716e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 8.1249e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00046673
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0011362
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 5.8974e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 1.873e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.5215e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.2942e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00021486
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.0284e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00045763
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00022859
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00026146
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0015401
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00032322
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 2.7977e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0013266
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0020116
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.041657
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0017581
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.028823
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0015995
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.05028
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.037848
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0040449
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.015342
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0021958
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.037153
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.090508
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0064649
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00027699
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0040363
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0097116
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.033152
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0017068
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.075953
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.035271
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.040342
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.23762
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.049872
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0043167
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.20469
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.15609
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.1103e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00098157
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00057319
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 7.4348e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00014045
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.1174e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.4896e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00013629
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00065872
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.995e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.001177
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00049972
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00041046
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0016809
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00044241
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 4.657e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0022715
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00018767
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00011868
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.5112e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.8849e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.9109e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.0876e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.7434e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 8.4266e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.5593e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.000151
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 6.3926e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 5.2508e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00021502
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 5.6595e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 5.9574e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00029057
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0020534
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0010459
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00016681
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00022549
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 4.152e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00011071
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00017907
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00086551
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.5819e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0015233
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0006566
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00053932
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0022085
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0005813
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 6.1189e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0029845
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.00078458
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 5.8176e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00098363
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 6.4889e-05
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.009968
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.005155
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.00073279
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.00095071
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0001749
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.001099
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0038117
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00017144
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 4.6164e-06
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.001592
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.002482
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.011996
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00038493
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.022711
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0091005
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.007475
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.030611
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0080569
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00084809
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.041366
HFTD - Distribution | HFTD - Distribution - 3QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0051648
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 7.5569e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00041557
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.4405e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.000104
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.0010863
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 2.4464e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 9.316e-08
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 8.3494e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 3.2448e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 3.0341e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 9.8024e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.5766e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 9.4188e-08
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.0902e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 4.7175e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 6.3814e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.3343e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0.00010198
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00024018
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 3.9853e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 6.4973e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.7478e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.9103e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.3348e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.8827e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 3.5078e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.4201e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.6243e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 9.5677e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.008e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.7381e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 8.2418e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00031078
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00029785
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.6381e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 7.7921e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.00070103
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 1.597e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 3.8523e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 3.7649e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.6369e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.2047e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 3.4826e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 5.8705e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 3.3878e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.985e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.8352e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 2.3675e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 4.4799e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 7.8388e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.0002044
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 3.4034e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 4.043e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.8865e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.0942e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.7353e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.2022e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 9.7997e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 3.974e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 4.5454e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00026774
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 5.6192e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 4.8637e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00023063
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00027825
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0038433
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.000196
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.001217
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0066407
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.00022852
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 1.3206e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00091818
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00041449
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00022264
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 9.102e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00013676
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 6.5917e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00073768
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.0003996
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00052686
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.6768e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.0011974
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0028716
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00045916
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.00066242
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00010237
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00022886
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00078123
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.6196e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0020557
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00083116
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00095066
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0055997
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0011752
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00010172
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0048236
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0039589
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.73395
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.050441
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.27692
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 1.4736
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.048626
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.010825
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.61432
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.25094
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.16108
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.072709
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.10101
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0054333
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.48908
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.29459
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.39921
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.042382
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.24494
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.63182
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.10265
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.08812
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.039504
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.087936
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.30018
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.017891
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.79613
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.31937
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.36529
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 2.1516
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.45158
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.039087
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 1.8535
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.80956
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 3.2559e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 5.7765e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0038665
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.0010323
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.001284
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00066469
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0014137
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 5.924e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0015781
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00087773
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00058004
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 4.8558e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0002794
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00040504
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0019577
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.2055e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0042512
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.0014851
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.0012199
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0049955
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.0013148
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.0001384
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0067507
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 1.2143e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00088629
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00026475
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0.00025916
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0.00012005
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00026758
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.0832e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00029323
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0.00017358
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0.0001094
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.2878e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.9709e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.7619e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00027849
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.0233e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00060374
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00021127
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0.00017353
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00071063
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0.00018704
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.9688e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00096031
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00022491
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.011678
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.003622
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0025878
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.0016952
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.003368
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00011387
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0029328
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.002042
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.0013153
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.6737e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00044946
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0006511
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.003147
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00011598
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0068429
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0023874
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0019609
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0080302
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0021136
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00022248
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.010852
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.013824
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0016691
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0094502
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.059782
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.0005177
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0028735
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.12179
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.034179
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.029181
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.021107
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.038772
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.001463
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.030308
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.023465
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.015535
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00066029
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0072456
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.026609
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0027221
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0014687
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.015581
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.022474
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.10862
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0040349
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.23806
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.082404
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.067685
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.27718
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.072954
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0076793
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.37456
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.026788
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 5.0526e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 6.037e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.7272e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.7307e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 1.6043e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 4.9767e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.4185e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.2183e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.4262e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 4.328e-08
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.5039e-08
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 5.4387e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 4.6544e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.8971e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 3.3966e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 6.5414e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 1.0347e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 7.359e-08
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.003e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.8972e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.4762e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.4315e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 1.527e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 6.8901e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 7.8808e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 4.642e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 9.7425e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 8.4327e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 3.9987e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00012162
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 4.4147e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.8303e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.2226e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 1.0742e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 3.2208e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 9.6067e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 5.1853e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 5.4637e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.4652e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 5.932e-08
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.1476e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.7093e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 7.0327e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 2.4669e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 4.8495e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 7.4351e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 4.7528e-08
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.2238e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.2566e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.7944e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 9.5602e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 4.2543e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.9091e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.1836e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00012862
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.6994e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.3365e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0001108
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 9.5584e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00068171
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 2.2871e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00022363
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.00016035
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 5.0235e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00027819
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00011298
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 1.4438e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 2.2856e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.8909e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 7.0327e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 3.7804e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 1.2373e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.0004672
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00081772
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00012313
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 1.7733e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.7461e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00013514
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00046133
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.4817e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0011044
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00049081
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00056138
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0033067
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00069399
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 6.0069e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0028484
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0015972
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.141
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0056524
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.052302
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.038876
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0011655
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.19201
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.077065
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.010352
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0017734
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0015163
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.036317
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.026078
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0085689
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.091908
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.16492
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.029047
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00029377
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.021835
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.051216
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.17483
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.009453
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.42066
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.18601
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.21275
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 1.2532
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.26301
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.022765
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 1.0795
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.30241
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.1769e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00112
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.0003876
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 6.0352e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 2.9348e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.3485e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 7.8727e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 8.6599e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.7244e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00012793
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00019652
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00094982
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.1367e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0018506
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00072056
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00059185
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0024237
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00063792
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 6.715e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0032753
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00022615
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 8.3865e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.1753e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 5.0506e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.7039e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.5803e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.6167e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 3.2496e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.8071e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.768e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00013379
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.4424e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.0002621
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 0.00010149
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 8.3364e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00034138
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 8.9853e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 9.4582e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00046133
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0035383
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00098724
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00016781
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 4.2567e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 4.6568e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0002796
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00019319
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 3.0889e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00025229
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00038448
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0018583
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.2306e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0036761
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0014098
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.001158
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0047419
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0012481
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00013138
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.006408
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0026557
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00018703
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0017849
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0015772
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 1.2408e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.038065
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.010497
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0018754
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0005148
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00058204
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0022505
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0020772
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.00033344
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0027187
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0069453
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00077028
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 4.8962e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0086118
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.013089
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.063264
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0021319
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.12578
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.047994
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.039421
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.16143
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.04249
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0044726
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.21815
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.010007
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 5.1451e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 3.6165e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.9905e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 2.3728e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 5.1261e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 7.7211e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.1749e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 6.7537e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.3014e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 2.7509e-08
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.227e-08
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 5.7884e-08
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 4.0975e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.0919e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 7.364e-08
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 3.0961e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 5.2066e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 5.2258e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 4.4277e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.665e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.5478e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 5.2837e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.9114e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 1.2956e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 5.6214e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 6.4296e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 3.7872e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 7.9485e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 6.8799e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 3.2624e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00010572
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 2.4388e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.9105e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.7e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 3.2847e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 5.168e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 4.8113e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.6984e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 5.0336e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 1.255e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 5.0548e-08
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 2.2665e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.5095e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 4.0575e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 2.4293e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 2.1382e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 3.6525e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 3.5884e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 2.683e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.8247e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.2326e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.4449e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.9791e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 3.5507e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.5372e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.7582e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00010356
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.1736e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.8814e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 8.9212e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 7.2118e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00046143
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00010726
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00026222
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 6.3245e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 8.8152e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00015168
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 7.9745e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 1.3228e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 3.805e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.4183e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 5.4834e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 4.0295e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 1.0011e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 3.9454e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00043924
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0006489
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 6.8634e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 4.8757e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.2233e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00012111
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00041342
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.2849e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0010168
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00043985
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00050309
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0029633
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00062193
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 5.3832e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0025527
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0014218
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.097913
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0072707
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.056217
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.015257
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.0024902
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.093696
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.051183
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0092479
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0031656
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0011893
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0046861
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.024109
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0068
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0035877
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.077893
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.13202
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.013889
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0010554
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.018741
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.043367
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.14804
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0082125
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.36546
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.1575
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.18015
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 1.0611
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.2227
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.019276
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.91407
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.26759
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.2168e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00054408
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00021487
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 5.5073e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 1.8653e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.1002e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 3.6406e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 5.9312e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.0316e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 6.6936e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00010655
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00016033
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00077493
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.6613e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0015702
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00058787
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00048287
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0019774
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00052046
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 5.4785e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0026722
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00011326
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 4.3643e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.0828e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 4.3262e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.304e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 7.2466e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.1107e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.8377e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.1225e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.4828e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.2288e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00010772
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.7077e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00021875
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 8.1721e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 6.7124e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00027488
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 7.235e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 7.6157e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00037146
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0019292
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00069685
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00015375
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 7.0865e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 3.4928e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 9.4724e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0001602
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 5.116e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 9.8499e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00022934
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00034456
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0016654
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.7364e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0033845
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0012634
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0010377
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0042496
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0011185
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00011774
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0057426
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0018441
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00024058
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0019185
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.00061898
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 2.6512e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.018575
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0069713
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0016754
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.00091896
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00045652
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0012618
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.001494
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00054163
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.00013961
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0023041
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0055598
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00036833
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 1.7589e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0073917
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.011083
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.053569
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0018522
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.10928
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.040639
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.03338
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.13669
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.035978
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0037872
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.18472
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0088544
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 3.7167e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 3.1091e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 3.8387e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.0094e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 1.9518e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.4315e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 9.2405e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 8.6896e-08
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 3.1443e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.0397e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 2.9037e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 4.7291e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 4.3409e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.6712e-08
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.5728e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.7207e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.9769e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.49e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 6.6306e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 3.1672e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 3.6226e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 2.1338e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 4.4783e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 3.8763e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.8381e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00010916
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 2.2323e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 2.7169e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 7.6026e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 1.4383e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.0293e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 3.9757e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 3.6153e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.4279e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 4.507e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 2.2211e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 3.5672e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 3.1458e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.1148e-08
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 9.8897e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.4114e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 8.2318e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.1287e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 1.8373e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 8.7579e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.0017e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 5.9003e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.2383e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.0719e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 5.0826e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 8.5179e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00054105
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 6.9675e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00022209
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 3.923e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00035014
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00013265
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 1.2392e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 7.043e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 1.2684e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00057733
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00099643
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 7.9695e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 1.8649e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.3924e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.1089e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00027681
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.4434e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00064233
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.0002945
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00033684
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0019841
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00041641
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 3.6043e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0017091
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0021623
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.068499
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0010117
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.028387
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0043734
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.14697
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.055177
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0048158
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.024607
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0050617
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.064009
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.12284
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.010762
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 2.3273e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0090244
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.021272
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.072615
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0038897
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.17309
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.077257
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.088364
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.52049
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.10924
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0094553
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.44836
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.25836
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.6014e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.001126
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00029399
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 3.6772e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 4.5515e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.9344e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.7113e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 9.0333e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00043661
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.362e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00080359
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00033122
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00027206
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0011141
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00029324
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 3.0867e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0015055
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00024232
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 6.4301e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 7.7772e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.0507e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 4.2628e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.0367e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.2698e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.1373e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.9185e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00011319
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 4.6559e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.8242e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00015661
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 4.1219e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 4.3389e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00021163
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0044534
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0011592
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00014403
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00028001
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 6.482e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00014895
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0002307
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0011151
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.6239e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0021381
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0008459
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00069481
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0028453
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00074889
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 7.8831e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.003845
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0012901
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 3.3476e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00096873
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.00017742
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.029136
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0075154
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.00087244
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0015249
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00040317
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0018934
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0051732
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00028538
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 3.8787e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0035593
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0054365
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.026276
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00087723
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.051756
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.019934
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.016373
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.06705
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.017648
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0018577
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.090608
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.008549
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 3.2154e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 1.0409e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.6722e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 3.6706e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 8.0406e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 6.8738e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 5.0661e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 5.5806e-08
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.2728e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 3.7874e-08
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 6.0831e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 1.8422e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 3.0221e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 2.8394e-09
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.2403e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.9348e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.0018e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.3272e-08
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 2.3706e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.0659e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.2191e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 7.1808e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.5071e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.3045e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 6.1857e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 5.263e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 7.8713e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.1964e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 2.5361e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 5.9406e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.6871e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.1103e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.2803e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 5.3937e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.5993e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 4.198e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 1.3275e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 2.1254e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.8721e-09
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.3407e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.8765e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.6887e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.4396e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 6.406e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.8606e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.2719e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.9272e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 4.0448e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.501e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.6601e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 3.8004e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00017461
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 3.4623e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 4.6019e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 1.3022e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 9.3695e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 7.1101e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 7.7347e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 1.9692e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 4.66e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 9.0862e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00038135
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 5.3474e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 3.0568e-08
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.1282e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.6158e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 8.9294e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.935e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00021961
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 9.5002e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00010866
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00064004
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00013433
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 1.1627e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00055134
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00091175
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.023874
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0028325
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0089779
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0016236
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.044222
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.026708
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0034422
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0086715
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0018903
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.014717
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.046821
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0062489
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 6.0741e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0033155
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0076825
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.026225
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0014512
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.064577
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.027901
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.031913
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.18798
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.039452
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0034148
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.16193
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.11441
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.3854e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00031831
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00016118
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 2.3616e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.8424e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 7.0468e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.9827e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.0399e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00014693
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.8696e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.0002873
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00011146
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 9.1555e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00037493
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 9.8682e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.0388e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00050666
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 6.3257e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 3.4131e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 4.9054e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.9689e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.5126e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.7148e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.1475e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.0046e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.6892e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 3.9466e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.5207e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.2491e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 5.1152e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.3463e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.4172e-06
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 6.9125e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0011917
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00062131
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 8.99e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 7.829e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 2.3814e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.9534e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.442e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0003597
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.239e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00073101
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00027287
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00022413
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00091785
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00024158
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 2.543e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0012403
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.00044965
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 9.3725e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00030638
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 6.5869e-05
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.008767
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0036378
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.00062359
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.00053737
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00015057
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.00043534
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0019718
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00016571
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 1.0123e-07
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0013077
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0019634
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0094898
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00032728
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.01931
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0071991
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0059132
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.024215
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0063735
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0006709
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.032723
HFTD - Distribution | HFTD - Distribution - 4QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0037858
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.3734e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00014709
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 9.4221e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.0001
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00015914
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 8.3465e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 1.9524e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 9.1485e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.7968e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 5.211e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.7483e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 4.7068e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 4.3057e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 6.5479e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 5.397e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 9.3324e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 6.277e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 8.7012e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 1.9624e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 5.5561e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 9.4217e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 2.3862e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.8266e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.4342e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.1964e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.2564e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 5.591e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.3368e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.6727e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 1.5743e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 3.3041e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.8599e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.3561e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 5.8818e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00012007
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 8.3165e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 8.2373e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.00012272
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 6.6429e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 8.9486e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 3.8708e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 8.3097e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.4984e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 7.7633e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 2.1008e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.8436e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 2.7616e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.4791e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 4.0157e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 2.8355e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.8301e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 1.6695e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 4.7185e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 7.4029e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 2.1579e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.6576e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.97e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.725e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.8494e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 1.713e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 7.1549e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 8.1835e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 4.8203e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.0117e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 8.7567e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 4.1523e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 5.0099e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.011557
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00016048
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0061187
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.017517
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.00075836
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 8.8898e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.00073365
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0021116
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00059034
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00080864
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00069956
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0002517
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 7.8729e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0030116
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00087475
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.0031643
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00028429
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.0025511
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0056715
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00096377
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 8.1315e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00011793
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00026514
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00090509
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.2966e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.002357
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00096294
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0011014
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0064875
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0013616
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00011785
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0055884
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0054832
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 3.0423
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.043117
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 1.6426
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 4.6032
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.20205
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.007565
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.61266
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 1.6698
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.45644
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.65526
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.56336
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.19893
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.064331
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 2.4343
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.6957
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 2.5549
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.23678
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.69693
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 1.4421
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.25021
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.02378
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.048768
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.10975
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.37464
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.021887
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.97398
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.39859
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.45589
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 2.6854
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.56359
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.048782
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 2.3132
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.3922
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 5.9172e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 1.2106e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 1.0511e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00083207
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00016579
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00073982
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00031916
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00038608
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 4.1183e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00078123
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00017364
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00057055
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 3.1666e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.5185e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.6648e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00032213
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.1485e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00067759
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00024437
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00020073
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00082199
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00021635
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.2774e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0011108
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 2.8207e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 2.2608e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00019562
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 4.0407e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0.000167
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 7.2415e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 8.4035e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 8.8297e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00018243
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.7982e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0.00013102
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.0856e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.0355e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.0374e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 5.0139e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.7887e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00010553
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 3.8037e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.1243e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00012794
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 3.3675e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.5447e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00017289
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.0001514
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.0023152
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.026858
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0051587
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0093987
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.013029
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0061987
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00136
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.011973
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.0044702
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.0078999
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00028416
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00051777
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00075433
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0036459
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00013298
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0078457
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0027659
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0022718
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0093034
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0024487
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00025776
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.012572
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.057299
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0014267
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.056055
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.18675
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0.0021512
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.0020081
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.030135
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.33104
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.06217
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.11871
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.16354
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.076364
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.017322
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.15085
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.055414
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.099419
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0036889
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.020616
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.060733
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0066354
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00039632
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.019234
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.028048
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.13557
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0049362
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.29124
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.10284
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.084474
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.34593
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.091049
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0095842
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.46747
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 1QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.046069
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 9.0836e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 1.0272e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.1392e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 4.9603e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 7.4052e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 2.2163e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 5.3817e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 2.3932e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 2.3599e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 5.8359e-09
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 4.1828e-09
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.1544e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 5.5465e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 2.2109e-09
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 7.084e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 1.1939e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 2.2542e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 5.3552e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.7876e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.955e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.3501e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.136e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 3.6205e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.4364e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.6429e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 9.6773e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.031e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.758e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 8.3361e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 2.6026e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 7.7356e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 9.8359e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 3.7789e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 5.9243e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 1.5366e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.4983e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.0642e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.0431e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 2.1654e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.6242e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.8869e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.2314e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 8.55e-09
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 5.5067e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 9.3365e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 1.8591e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 4.0921e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.3221e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.1777e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.0202e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.4219e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 1.0778e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 4.2772e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 4.8921e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 2.8816e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 6.0478e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 5.2347e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 2.4823e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 2.107e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00064467
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 2.2898e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00031425
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 5.6225e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 2.3589e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00034147
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00013888
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 1.3432e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 9.2384e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 2.4962e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 6.5587e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 3.2381e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 1.5189e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00030317
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00087192
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.00013304
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 3.3845e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.9707e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00013261
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00045267
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.7091e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0012055
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.0004816
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00055084
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0032446
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00068097
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 5.8942e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.002795
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0014245
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.16884
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0061619
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.082738
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.013883
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.00059748
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.27037
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.10996
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.010614
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0071275
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0019274
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.050717
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.025065
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0011725
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.073984
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.22397
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.034663
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00092536
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.024641
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.054716
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.18678
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.011182
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.4976
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.19872
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.22729
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 1.3388
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.28098
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.024321
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 1.1533
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.35379
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 3.9137e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00024922
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 7.614e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 9.9867e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 3.9572e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 3.7505e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.671e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.032e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 2.0096e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.8576e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.0968e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00019801
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.437e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00043879
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00015022
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00012338
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00050527
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00013299
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.3999e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0006828
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 5.8812e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.7213e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.2439e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 7.4644e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 7.4031e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.596e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.1105e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 3.9507e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.3249e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.2014e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.9973e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.1254e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 6.64e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.2738e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.8677e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 7.6483e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.0131e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.119e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00010336
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0043432
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0012136
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00015611
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00017206
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 6.1476e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00026076
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00016548
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 3.7919e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00026215
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00037727
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0018235
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.8014e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0040128
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0013833
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0011362
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0046529
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0012247
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.00012891
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0062878
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0031799
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00020389
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0028235
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.00056323
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 6.3612e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.053602
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.014977
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0019229
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0020691
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00073985
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0031429
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0019965
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 4.5627e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.0021885
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0094322
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00091921
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 1.5423e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0097187
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.013984
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.067588
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0025219
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.14879
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.051273
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.042115
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.17246
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.045393
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0047782
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.23306
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 2QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.011707
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 7.7611e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 3.9072e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.1858e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 2.2053e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 2.9099e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 2.9419e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.0513e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 5.8612e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 9.1186e-09
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 4.4387e-09
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 2.3862e-10
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 3.5724e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.1545e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.2655e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 1.4544e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 4.4073e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 5.9769e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 8.6456e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.4991e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.5004e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 5.1217e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.8538e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 1.27e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 5.449e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 6.2325e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 3.6711e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 7.7047e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 6.6689e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 3.1623e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 9.0673e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 3.3236e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 9.946e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.94e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 2.5211e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 2.6407e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 9.3783e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.6434e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 3.8312e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.212e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.1891e-09
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.8059e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 5.177e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 6.3066e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 1.157e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 3.5923e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 4.997e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 6.7154e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.9524e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.5023e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.5369e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.5818e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 3.8189e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.6351e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.8702e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.1016e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.312e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.0012e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 9.4896e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 7.4852e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00030841
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 1.5617e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00011584
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 2.4698e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 1.4281e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00015686
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 4.9392e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 6.8952e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.6011e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 8.6072e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 1.9609e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 7.4789e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 4.5649e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 8.0881e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00042198
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 3.6735e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 3.5659e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.6638e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.1131e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00020868
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.1758e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00052321
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00022202
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00025394
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0014958
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00031393
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 2.7172e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0012885
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00058174
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.072927
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0040643
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.027551
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0063439
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.00042849
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.12016
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.039038
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0056355
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.001464
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 7.8702e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.014912
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.005685
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.004174
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.020988
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.10127
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0095124
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0009449
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.010851
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.024916
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.085054
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0047869
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.21302
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.09049
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.1035
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.60965
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.12795
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.011075
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.52516
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.14514
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 3.3439e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 9.4991e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.8648e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 3.8588e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 3.98e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.5008e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 5.1712e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.148e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 1.1503e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.0389e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.5541e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 7.5116e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.6086e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00015391
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 5.6985e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 4.6806e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00019168
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 5.045e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 5.3105e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00025902
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.2077e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 4.2752e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 8.2418e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.0082e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 3.802e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.3289e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 4.8965e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 2.9141e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.5866e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.3708e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.1459e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.9878e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 2.3528e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 8.6928e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 7.1401e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 2.9239e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 7.6959e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 8.1009e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 3.9513e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0019951
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00043161
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 8.0141e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 3.943e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 1.4869e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 7.7961e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 3.8219e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 1.1396e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00011696
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00017392
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00084061
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.9519e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0017416
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0006377
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0005238
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.002145
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00056457
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 5.9429e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0028987
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.0013735
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.00013449
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00094021
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.00025737
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 4.562e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.023822
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0053172
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0010209
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00056196
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 2.1191e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.00092409
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00045282
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.00016242
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.00062085
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0042647
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00025226
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 1.5748e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0042796
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0063677
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.030777
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0010796
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.063696
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.023348
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.019178
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.078535
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.020671
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0021759
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.10613
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 3QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0048026
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 6.7319e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 1.8039e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.7056e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.2962e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 1.1826e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 7.0065e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 9.0055e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 4.008e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 1.5783e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 2.1088e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.4465e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 1.0213e-11
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.4759e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 5.8103e-09
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 8.6862e-09
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.7847e-10
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 1.7076e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 2.8547e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 5.2916e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 4.8813e-09
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.3391e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.8885e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.6928e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.4362e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 6.3911e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.865e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 3.2769e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 1.9302e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 4.051e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 3.5064e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.6627e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 5.7353e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 1.3937e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.9197e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 9.5452e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 8.5092e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 5.0855e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 3.7904e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.6555e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 6.3939e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 8.5882e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 5.8868e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 3.9628e-11
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 6.2298e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.305e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 3.5336e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.2685e-10
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 1.3537e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 2.1734e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 4.2516e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 3.3703e-09
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 9.4246e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.2316e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 7.6179e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.0453e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 1.8002e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 8.1048e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 9.2701e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 5.4603e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.146e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 9.9193e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 4.7036e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 4.3584e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00021417
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 5.9031e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00011289
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 6.4523e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 3.0973e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 9.7172e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 3.9134e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 6.7691e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 6.6823e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 4.5677e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 3.4126e-09
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 1.641e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 4.0228e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 2.7843e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.6269e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00012783
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00030016
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 4.711e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 8.7128e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.5794e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.7432e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00012778
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.7733e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00030141
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00013594
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00015549
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00091588
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00019222
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 1.6638e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00078896
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00053627
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.053032
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0014745
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.028933
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.016785
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.00083895
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.074009
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.029773
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0051062
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.0056565
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0038643
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 2.6302e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.012348
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0030569
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.002347
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 4.7681e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.029781
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.07418
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.011963
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00021985
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0061839
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.014611
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.049876
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0026596
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.11835
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.053064
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.060693
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.3575
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.075031
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0064944
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.30796
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.1277
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 2.9005e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 4.1703e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.2752e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 6.6788e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 1.43e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.297e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 6.4235e-09
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.1365e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.0811e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 7.8954e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 6.4948e-09
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.3377e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.1712e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.9494e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.3128e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 7.7456e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.9961e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.461e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00010078
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.6525e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.7921e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00013619
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 8.923e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.6776e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.3755e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 2.9604e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.6833e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 1.267e-09
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.5842e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.1802e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.6327e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.3447e-09
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 7.6588e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.1751e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 5.6796e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.8798e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 1.1091e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 4.3087e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.5391e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.4493e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 3.8146e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 4.0153e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.9585e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0012359
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00034197
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 7.8676e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.00012445
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00011249
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 5.8952e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 6.5244e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 2.0557e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 6.951e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.6243e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.9344e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00010649
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00051472
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.7005e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0010033
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00039048
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00032073
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0013134
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0003457
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 3.6389e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0017749
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.00099883
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 4.879e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00098738
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.00068097
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 8.9321e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.014672
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0040552
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.00092506
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.001642
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0014834
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 7.0821e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0007652
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00024349
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 9.133e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 7.4285e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.00088093
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.003124
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00031724
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 3.6641e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.002439
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0037341
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.018048
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00059982
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.035389
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.013692
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.011246
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.046054
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.012121
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0012759
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.062235
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 4QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0042256
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.3117e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 3.3006e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.4019e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 7.8189e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 2.1876e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.1124e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 5.5938e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 5.2014e-09
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 3.7003e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 5.8185e-09
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | other | all other | 1.5602e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 3.3021e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 5.4564e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 2.8513e-10
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.0333e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.2967e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.8081e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.9233e-09
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 3.5259e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.9237e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.2002e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 1.296e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.72e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.3543e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.1164e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 9.1982e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 2.4578e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.7753e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 6.09e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 1.6378e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 4.7651e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.3905e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.2771e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.7845e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.4554e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | other | all other | 1.1692e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 2.5363e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 4.0317e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 2.0314e-10
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.9501e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.5492e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 5.2883e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.3201e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 1.0324e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 5.6263e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 6.4352e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 3.7905e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 7.9554e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 6.8859e-08
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 3.2652e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 6.9748e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.00022139
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 5.528e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 7.1125e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 2.2021e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 8.4873e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 4.4393e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 3.6047e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 3.0795e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 3.3717e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | other | all other | 0.00010826
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00033495
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 4.1699e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 1.4888e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.0846e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.6086e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 8.9048e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.5879e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00020416
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 9.4739e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00010836
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00063827
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00013396
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 1.1595e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00054982
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00064862
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.045613
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0014739
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.015075
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.0050285
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.059878
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.030647
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0024761
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.021592
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0023467
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | other | all other | 0.022807
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.074316
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0086024
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.000453
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0041427
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.009805
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.033471
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0017789
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.079159
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.03561
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.04073
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.23991
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.050351
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0043582
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.20666
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.1336
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 5.6514e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 5.1515e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.7797e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 2.2011e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 5.3563e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.0826e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.2503e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.4865e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.6518e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.2426e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 4.2731e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.0117e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.6524e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 6.7667e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.781e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.8748e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 9.1442e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.1218e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 3.8662e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 4.8985e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.3131e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.3224e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.8353e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.1574e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.9428e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.0781e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 6.3607e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.9911e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.4568e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.0061e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.648e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.7874e-07
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.3596e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | animal contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | balloon contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | other contact from object | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0010795
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00038793
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 4.1897e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00012243
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 1.723e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | other | all other | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | unknown | unknown | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.762e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.4215e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0003587
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.1519e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00067959
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00027212
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00022352
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00091532
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00024091
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | grow into | 2.5359e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0012369
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | animal contact | 0.00085909
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | balloon contact | 4.8772e-05
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00051444
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.000204
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | contamination | contamination | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.011871
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.0041742
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.00044858
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.001338
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00018692
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | other | all other | 0.00067465
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | unknown | unknown | 0.0031298
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.00022812
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 7.5499e-06
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0016339
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0025058
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.012112
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00040118
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.02367
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | dead | 0.009188
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0075469
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.030905
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0081344
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00085625
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.041764
HFTD - Distribution | HFTD - Distribution - 5QU CoRE ¦ 5QU LoRE | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0044208
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0066569
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.3772
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.004302
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.89003
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.018969
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.9246
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.0027258
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.56394
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.042983
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 8.8926
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.0098463
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 2.0371
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0074728
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 1.546
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.052161
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 10.7916
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0093086
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 1.9258
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 0.012183
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 2.5205
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.092344
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 19.1049
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00019885
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.6814e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0025566
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.26461
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.1712e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.7632e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00079344
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.082121
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0003977
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00011363
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0051133
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.52923
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.0571e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.8773e-06
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00026448
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.027374
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00067883
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00019395
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.0087278
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.90333
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00019199
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | dead | 5.4855e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | dead | 0.0024685
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | dead | 0.25549
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 8.914e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.5468e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.0011461
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.11862
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.0003977
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00011363
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0051133
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.52923
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00012342
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 3.5264e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.0015869
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.16424
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0.00021256
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 6.0733e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | grow into | 0.002733
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.28286
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0017211
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.00049174
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.022128
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 2.2903
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | other | all other | 6.1134e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | other | all other | 1.7467e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | other | all other | 0.00078601
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | other | all other | 0.081352
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 2.5898e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 7.3995e-06
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.00033298
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.034463
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0.00031726
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 9.0644e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.004079
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 0.42218
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0018906
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00054017
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.024308
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 2.5158
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.0007381
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00021089
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0094899
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.98221
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0.00010359
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 2.9598e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.0013319
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.13785
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0.00020719
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 5.9196e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.0026638
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 0.27571
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00016187
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 4.6247e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0020811
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.2154
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0.00012949
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 3.6998e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0.0016649
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 0.17232
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00079638
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00022754
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.010239
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 1.0597
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00025251
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 7.2146e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.0032466
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.33602
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 5.8271e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 1.6649e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0.0007492
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 0.077543
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 6.4746e-06
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 1.8499e-06
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 8.3245e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0.0086158
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 7.7695e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 2.2199e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0.00099894
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 0.10339
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0.00054387
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0.00015539
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.0069926
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.72373
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 5.8271e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.6649e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0007492
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.077543
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00070741
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00020212
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | contact from object | animal contact | 0.0090953
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | contact from object | animal contact | 0.94136
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0.00023289
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 6.6541e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | contact from object | balloon contact | 0.0029943
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.30991
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00026783
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 7.6522e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0034435
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.3564
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0.00055312
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0.00015803
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0071115
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.73604
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | contamination | contamination | 2.3289e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | contamination | contamination | 6.6541e-06
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | contamination | contamination | 0.00029943
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | contamination | contamination | 0.030991
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00017758
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | unknown | unknown | 5.0737e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | unknown | unknown | 0.0022832
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | unknown | unknown | 0.23631
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 2.9112e-06
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 8.3176e-07
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 3.7429e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.0038739
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 3.2023e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 9.1493e-06
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.00041172
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.042613
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 2.3289e-05
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 6.6541e-06
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.00029943
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.030991
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | other | all other | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | other | all other | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | other | all other | 0.016441
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | other | all other | 3.4014
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | anchor / guy damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | anchor / guy damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | anchor / guy damage or failure | 0.0030395
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | anchor / guy damage or failure | 0.62883
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | capacitor bank damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | capacitor bank damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | capacitor bank damage or failure | 0.037233
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | capacitor bank damage or failure | 7.7032
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.22188
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 45.9047
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.086625
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 17.9217
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.012158
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 2.5153
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | fuse damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | fuse damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | fuse damage or failure | 0.024316
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | fuse damage or failure | 5.0306
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.018997
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 3.9302
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | lightning arrestor damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | lightning arrestor damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | lightning arrestor damage or failure | 0.015197
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | lightning arrestor damage or failure | 3.1442
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.093463
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 19.3365
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.029635
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 6.1311
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | recloser damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | recloser damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | recloser damage or failure | 0.0068388
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | recloser damage or failure | 1.4149
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | sectionalizer damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | sectionalizer damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | sectionalizer damage or failure | 0.00075987
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | sectionalizer damage or failure | 0.15721
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | switch damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | switch damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | switch damage or failure | 0.0091184
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | switch damage or failure | 1.8865
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.063829
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 13.2054
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0068388
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 1.4149
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.19024
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 39.3593
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.062632
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 12.9578
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.072026
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 14.9015
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.14875
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 30.7748
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.0062632
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | contamination | contamination | 1.2958
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.047757
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | unknown | unknown | 9.8803
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | utility work / operation | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | utility work / operation | utility work / operation | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | utility work / operation | utility work / operation | 0.0007829
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | utility work / operation | utility work / operation | 0.16197
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.0086119
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 1.7817
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | wire-to-wire contact | wire-to-wire contact / contamination | 0.0062632
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | wire-to-wire contact | wire-to-wire contact / contamination | 1.2958
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | wire-to-wire contact | 0 | 0
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | wire-to-wire contact | 0 | 0
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | wire-to-wire contact | 0 | 0
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | wire-to-wire contact | 0 | 0
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Catastrophic Fires | utility work / operation | 0 | 0
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Destructive Fires | utility work / operation | 0 | 0
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Large Fires | utility work / operation | 0 | 0
non-HFTD - Distribution | non-HFTD - Distribution | Red Flag Warning - Small Fires | utility work / operation | 0 | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | wire-to-wire contact | 0 | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | wire-to-wire contact | 0 | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | wire-to-wire contact | 0 | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | wire-to-wire contact | 0 | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Catastrophic Fires | utility work / operation | 0 | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Destructive Fires | utility work / operation | 0 | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Large Fires | utility work / operation | 0 | 0
non-HFTD - Distribution | non-HFTD - Distribution | Non-Red Flag Warning - Small Fires | utility work / operation | 0 | 0
non-HFTD - Distribution | non-HFTD - Distribution | Seismic - Non-Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 0
non-HFTD - Distribution | non-HFTD - Distribution | Seismic - Red Flag Warning - Catastrophic Fires | cc - seismic scenario | seismic scenario | 1.576e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.1868e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.1868e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.8681e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0049252
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.4196e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.4196e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.2776e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0021939
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.0879e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.0879e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 9.7907e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.016813
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.3736e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.3736e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.7362e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00098504
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 2.8362e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 2.8362e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00025526
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.043834
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.1574e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.1574e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 0.00010416
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.017887
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.2023e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.2023e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00010821
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.018581
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 7.7975e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 7.7975e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00070177
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.12051
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.5731e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.5731e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00014158
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.024312
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.3616e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.3616e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 1.2255e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.0021044
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 6.7169e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 6.7169e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00060452
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.10381
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.2408e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.0344e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.2064e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0008528
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.8272e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.896e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.1376e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00056853
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00034997
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.9996e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00029997
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0041219
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.2068e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.724e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.0344e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00014213
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00071201
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0.00010172
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00061029
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.0083859
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0.00026549
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | dead | 3.7928e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | dead | 0.00022757
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0031269
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0.00020515
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.9308e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 0.00017585
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0024163
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00089303
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0.00012758
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00076545
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.010518
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0.00022929
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 3.2756e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 0.00019654
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0027005
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.4136e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.448e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | grow into | 2.0688e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00028427
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.0012068
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0.0001724
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.0010344
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.014213
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.4508e-07
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.4508e-07
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.6057e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.0013061
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.7645e-07
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.7645e-07
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.388e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.0005818
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.8848e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.8848e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.5963e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.0044585
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.6902e-07
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.6902e-07
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.5211e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 0.00026121
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 7.5212e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 7.5212e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 6.7691e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.011624
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 3.0692e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 3.0692e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 2.7623e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 0.0047434
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 3.1883e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.1883e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 2.8694e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.0049275
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 2.0678e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 2.0678e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.0001861
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.031957
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 4.1716e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 4.1716e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 3.7545e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0064473
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 3.6108e-07
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 3.6108e-07
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 3.2497e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00055805
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.7812e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.7812e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00016031
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.027528
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.7193e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.8847e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.3308e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00032027
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.8128e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.5898e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.5539e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00021351
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00013143
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.8776e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00011266
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.001548
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.5321e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.4744e-07
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.8847e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.3378e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00026739
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 3.8199e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00022919
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.0031493
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 9.9706e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.4244e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | dead | 8.5462e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | dead | 0.0011743
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 7.7046e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.1007e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 6.6039e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.00090743
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00033538
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 4.7911e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00028746
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.00395
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 8.611e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.2301e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 7.3809e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.0010142
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 9.0642e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.2949e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | grow into | 7.7693e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | grow into | 0.00010676
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00045321
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 6.4744e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00038847
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.0053378
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.041e-09
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.041e-09
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.6369e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.2453e-06
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.8001e-09
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.8001e-09
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.6201e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.782e-06
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.3794e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.3794e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.2415e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.1319e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.082e-10
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.082e-10
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.2738e-09
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.2491e-06
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 3.5965e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 3.5965e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 3.2368e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 5.5584e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.4676e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.4676e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 1.3209e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 2.2682e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.5246e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.5246e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 1.3721e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 2.3562e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 9.8875e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 9.8875e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 8.8988e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.00015281
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.9948e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.9948e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 1.7953e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 3.0829e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.7266e-09
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.7266e-09
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 1.5539e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 2.6685e-06
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 8.5173e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 8.5173e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 7.6656e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.00013163
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.022e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.6029e-09
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.1617e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.0926e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.0147e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.7353e-09
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.4412e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.7284e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.9106e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.1581e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.4948e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.4281e-06
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.0037e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.4338e-09
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.6029e-09
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.1821e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 5.9217e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 8.4595e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 5.0757e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 6.9744e-06
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.2081e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | dead | 3.1544e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | dead | 1.8926e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | dead | 2.6006e-06
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.7062e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.4375e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 1.4625e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 2.0096e-06
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 7.4272e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.061e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 6.3661e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 8.7475e-06
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.907e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.7242e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 1.6345e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 2.246e-06
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.0073e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.8676e-09
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | grow into | 1.7206e-08
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | grow into | 2.3642e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.0037e-06
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.4338e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 8.6029e-07
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 1.1821e-05
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 2.62e-05
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | animal contact | 7.4858e-06
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | animal contact | 0.00033686
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | animal contact | 0.034832
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 8.7335e-06
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 2.4953e-06
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00011229
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.011611
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.4556e-05
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 4.1588e-06
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00018715
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.019351
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 1.1645e-05
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 3.327e-06
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.00014972
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.015481
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contamination | contamination | 2.9112e-06
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | contamination | contamination | 8.3176e-07
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | contamination | contamination | 3.7429e-05
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | contamination | contamination | 0.0038702
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 6.4746e-06
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.8499e-06
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 8.3245e-05
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0086075
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.2949e-05
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 3.6998e-06
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00016649
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.017215
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 6.4746e-06
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.8499e-06
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 8.3245e-05
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0086075
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | unknown | unknown | 8.7335e-06
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | unknown | unknown | 2.4953e-06
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | unknown | unknown | 0.00011229
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | unknown | unknown | 0.011611
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0070461
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 1.4578
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.0023487
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.48592
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0039145
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.80986
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0031316
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.64789
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 0
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.0007829
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.16197
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00075987
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.15721
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0015197
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.31442
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00075987
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.15721
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0023487
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.48592
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 3.7845e-05
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | animal contact | 1.0813e-05
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | contact from object | animal contact | 0.00048658
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | contact from object | animal contact | 0.050312
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 8.7335e-06
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 2.4953e-06
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00011229
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.011611
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 2.0378e-05
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 5.8223e-06
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.000262
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.027091
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | contamination | contamination | 2.9112e-06
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | contamination | contamination | 8.3176e-07
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | contamination | contamination | 3.7429e-05
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | contamination | contamination | 0.0038702
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.9424e-05
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 5.5497e-06
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00024973
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.025823
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 6.4746e-06
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.8499e-06
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 8.3245e-05
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0086075
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 6.4746e-06
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.8499e-06
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 8.3245e-05
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0086075
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 6.4746e-06
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.8499e-06
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 8.3245e-05
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0086075
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 6.4746e-06
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.8499e-06
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 8.3245e-05
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0086075
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | unknown | unknown | 2.9112e-06
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | unknown | unknown | 8.3176e-07
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | unknown | unknown | 3.7429e-05
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | unknown | unknown | 0.0038702
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.010178
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 2.1056
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0023487
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.48592
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0054803
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 1.1338
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 0
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.0007829
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.16197
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0022796
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.47162
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00075987
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.15721
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00075987
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.15721
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00075987
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.15721
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00075987
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.15721
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0007829
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.16197
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | contamination | contamination | 2.9112e-06
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Destructive Fires | contamination | contamination | 8.3176e-07
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Large Fires | contamination | contamination | 3.7429e-05
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Small Fires | contamination | contamination | 0.0038702
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 6.4746e-06
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.8499e-06
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 8.3245e-05
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0086075
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 2.9112e-06
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 8.3176e-07
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 3.7429e-05
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0038702
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 0
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.0007829
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.16197
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00075987
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.15721
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.0007829
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.16197
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0034676
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0011928
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 3.3894e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00049537
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.0001704
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | animal contact | 4.842e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | animal contact | 0.0029722
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | animal contact | 0.0010224
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | animal contact | 2.9052e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | animal contact | 0.040841
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | animal contact | 0.014049
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | animal contact | 3.992e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0.00028897
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 9.9402e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.8245e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 4.1281e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.42e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 4.035e-08
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00024769
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | balloon contact | 8.5202e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | balloon contact | 2.421e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0034034
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0011707
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | balloon contact | 3.3266e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.0008669
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00029821
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 8.4735e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.00012384
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 4.2601e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.2105e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00074306
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00025561
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | other contact from object | 7.263e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.01021
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0035122
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | other contact from object | 9.9799e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0024819
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00085374
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.4259e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00035455
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00012196
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 3.4656e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0021273
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00073178
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 2.0793e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.029231
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.010055
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 2.8572e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0016546
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00056916
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.6173e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00023637
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 8.1309e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.3104e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0014182
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00048785
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.3862e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.019487
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0067035
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 1.9048e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0024819
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00085374
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.4259e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00035455
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00012196
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.4656e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0021273
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00073178
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 2.0793e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.029231
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.010055
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 2.8572e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00028897
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | unknown | unknown | 9.9402e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | unknown | unknown | 2.8245e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | unknown | unknown | 4.1281e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | unknown | unknown | 1.42e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Destructive Fires | unknown | unknown | 4.035e-08
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | unknown | unknown | 0.00024769
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | unknown | unknown | 8.5202e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Large Fires | unknown | unknown | 2.421e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | unknown | unknown | 0.0034034
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | unknown | unknown | 0.0011707
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Small Fires | unknown | unknown | 3.3266e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00092467
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00031808
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 9.0382e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00092467
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00031808
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 9.0382e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.008322
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0028627
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 8.1343e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 1.4291
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.49159
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.0013968
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 7.7056e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.6507e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 7.5318e-08
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 7.7056e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 2.6507e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 7.5318e-08
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.0006935
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00023856
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 6.7786e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.11909
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.040966
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0001164
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00023117
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 7.952e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 2.2595e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.00023117
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 7.952e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 2.2595e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0020805
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00071568
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 2.0336e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.35727
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.1229
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00034921
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00021687
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 7.4602e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.1198e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00021687
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 7.4602e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.1198e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0019518
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00067142
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 1.9078e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.33518
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.1153
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.00032762
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00014458
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 4.9735e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.4132e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00014458
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 4.9735e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.4132e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0013012
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00044761
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.2719e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.22345
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.076865
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00021841
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00021687
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 7.4602e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.1198e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00021687
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 7.4602e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.1198e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0019518
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00067142
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 1.9078e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.33518
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.1153
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.00032762
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 7.7056e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 2.6507e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 7.5318e-08
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 7.7056e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 2.6507e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 7.5318e-08
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0006935
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00023856
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | unknown | unknown | 6.7786e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.11909
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.040966
HFTD - Transmission | HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.0001164
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0.00029473
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 9.3401e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 5.1927e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 4.2104e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.3343e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 7.4181e-08
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00025263
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | contact from object | balloon contact | 8.0058e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Large Fires | contact from object | balloon contact | 4.4509e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0034713
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0011001
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Small Fires | contact from object | balloon contact | 6.1158e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00029473
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 9.3401e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 5.1927e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 4.2104e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.3343e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 7.4181e-08
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00025263
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | contact from object | other contact from object | 8.0058e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Large Fires | contact from object | other contact from object | 4.4509e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0034713
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0011001
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Small Fires | contact from object | other contact from object | 6.1158e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00084379
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0002674
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.4866e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00012054
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 3.82e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.1237e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00072325
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0002292
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 1.2742e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.009938
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0031494
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 1.7509e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0016876
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0005348
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.9732e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00024108
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 7.64e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.2475e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0014465
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0004584
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 2.5485e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.019876
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0062987
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 3.5018e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00058946
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.0001868
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | unknown | unknown | 1.0385e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | unknown | unknown | 8.4209e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | unknown | unknown | 2.6686e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Destructive Fires | unknown | unknown | 1.4836e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | unknown | unknown | 0.00050525
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | unknown | unknown | 0.00016012
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Large Fires | unknown | unknown | 8.9017e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | unknown | unknown | 0.0069426
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | unknown | unknown | 0.0022001
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Small Fires | unknown | unknown | 1.2232e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 7.8593e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.4906e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.3847e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 7.8593e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 2.4906e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.3847e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00070734
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00022416
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 1.2462e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.12147
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.038493
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.000214
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 7.8593e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 2.4906e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.3847e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 7.8593e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 2.4906e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.3847e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00070734
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00022416
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 1.2462e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.12147
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.038493
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.000214
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 7.3733e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.3366e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.299e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 7.3733e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.3366e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.299e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00066359
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00021029
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 1.1691e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.11395
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.036112
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.00020077
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00014747
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 4.6732e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.5981e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00014747
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.6732e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.5981e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0013272
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00042059
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 2.3383e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.22791
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.072225
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.00040154
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00015719
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 4.9813e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 2.7694e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00015719
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 4.9813e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 2.7694e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0014147
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00044831
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | unknown | unknown | 2.4924e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.24293
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.076985
HFTD - Transmission | HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.000428
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0039895
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0010579
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 5.0588e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00056992
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00015113
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | animal contact | 7.2269e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | contact from object | animal contact | 0.0034195
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | contact from object | animal contact | 0.00090681
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | contact from object | animal contact | 4.3361e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | contact from object | animal contact | 0.046987
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | contact from object | animal contact | 0.01246
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | contact from object | animal contact | 5.9582e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00092065
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00024414
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.1674e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.00013152
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 3.4877e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.6677e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00078913
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00020926
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | contact from object | other contact from object | 1.0006e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.010843
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0028754
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | contact from object | other contact from object | 1.375e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0026357
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00069895
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 3.3422e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00037653
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 9.985e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 4.7746e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0022592
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0005991
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 2.8648e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.031043
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0082321
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 3.9364e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00087858
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00023298
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.1141e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00012551
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 3.3283e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.5915e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00075307
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0001997
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 9.5492e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.010348
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.002744
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 1.3121e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0017572
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00046597
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 2.2281e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00025102
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 6.6567e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 3.1831e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0015061
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0003994
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.9098e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.020695
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0054881
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 2.6243e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0017572
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00046597
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.2281e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00025102
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 6.6567e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.1831e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0015061
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0003994
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 1.9098e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.020695
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0054881
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 2.6243e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00087858
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00023298
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.1141e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0.00012551
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.3283e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.5915e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00075307
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.0001997
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 9.5492e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.010348
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.002744
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 1.3121e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | other | all other | 0.00030688
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | other | all other | 8.138e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | other | all other | 3.8914e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | other | all other | 4.384e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | other | all other | 1.1626e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | other | all other | 5.5591e-08
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | other | all other | 0.00026304
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | other | all other | 6.9754e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | other | all other | 3.3355e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | other | all other | 0.0036144
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | other | all other | 0.00095848
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | other | all other | 4.5832e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0.00030688
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 8.138e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 3.8914e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 4.384e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.1626e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 5.5591e-08
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.00026304
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 6.9754e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 3.3355e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0036144
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00095848
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 4.5832e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0010638
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00028211
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 1.349e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.0010638
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00028211
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 1.349e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0095745
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.002539
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 1.2141e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 1.6441
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.436
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.0020849
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.0002455
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 6.5102e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 3.113e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.0002455
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 6.5102e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 3.113e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0022095
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00058592
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 2.8017e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.37942
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.10062
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00048112
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00023032
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 6.1076e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.9205e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00023032
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 6.1076e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.9205e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0020729
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00054969
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 2.6285e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.35596
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.094394
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.00045137
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 7.6773e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 2.0359e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 9.7351e-08
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 7.6773e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.0359e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 9.7351e-08
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00069095
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00018323
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 8.7616e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.11865
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.031465
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.00015046
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00015355
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 4.0718e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.947e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00015355
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 4.0718e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.947e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0013819
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00036646
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.7523e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.2373
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.062929
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00030091
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00015355
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 4.0718e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.947e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00015355
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.0718e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.947e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0013819
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00036646
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 1.7523e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.2373
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.062929
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.00030091
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 7.6773e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.0359e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 9.7351e-08
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 7.6773e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.0359e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 9.7351e-08
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00069095
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00018323
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 8.7616e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.11865
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.031465
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00015046
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | other | all other | 8.1833e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | other | all other | 2.1701e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | other | all other | 1.0377e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | other | all other | 8.1833e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | other | all other | 2.1701e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | other | all other | 1.0377e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | other | all other | 0.0007365
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | other | all other | 0.00019531
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | other | all other | 9.3391e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | other | all other | 0.12647
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | other | all other | 0.033539
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | other | all other | 0.00016037
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 8.1833e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 2.1701e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.0377e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 8.1833e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 2.1701e-05
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.0377e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.0007365
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.00019531
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 9.3391e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.12647
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.033539
HFTD - Transmission | HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00016037
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.9552e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.5838e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.7931e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.9768e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.6759e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.7861e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00023028
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.5764e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.3035e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.7225e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.8621e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.3179e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.1173e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.1907e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00015352
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.3843e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 9.4501e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.6988e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.35e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.8554e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 8.1001e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.3133e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.001113
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00031786
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.2587e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 9.3063e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.6552e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.3295e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.7931e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.9768e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.838e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.0961e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00019226
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 5.4907e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 2.7466e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 7.8438e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00016479
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 4.7063e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.0022644
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.00064668
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 7.169e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.0474e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.0241e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.9248e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | dead | 6.1449e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | dead | 1.7549e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | dead | 0.00084435
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | dead | 0.00024114
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 5.5397e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.5821e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 7.9139e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.2601e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 4.7483e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 1.3561e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.00065246
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.00018633
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00024114
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 6.8866e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 3.4449e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 9.838e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00020669
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 5.9028e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.0028401
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.00081109
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 6.1914e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.7682e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 8.8449e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.526e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 5.307e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 1.5156e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.00072922
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.00020825
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 6.5173e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.8613e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 9.3104e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.6589e-07
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | grow into | 5.5863e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | grow into | 1.5954e-06
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | grow into | 7.6759e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | grow into | 2.1921e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00032587
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 9.3063e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 4.6552e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.3295e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00027931
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 7.9768e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.003838
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.0010961
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.486e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.9096e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.1229e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.5851e-07
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.2737e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.3511e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00017502
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.6046e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 9.9066e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.6064e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.4152e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.7234e-07
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.4914e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.2341e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00011668
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.0698e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 7.1823e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.8896e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.026e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.6995e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.1563e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.6197e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00084592
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00022256
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.4767e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.516e-07
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.5381e-07
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 9.3085e-08
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.1229e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.5851e-07
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.917e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.6744e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00014612
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 3.8444e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 2.0875e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 5.492e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00012525
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 3.2952e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.001721
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.00045279
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 5.4487e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.4335e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | dead | 7.7838e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.0479e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | dead | 4.6703e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | dead | 1.2287e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | dead | 0.00064173
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | dead | 0.00016884
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 4.2103e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.1077e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 6.0148e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.5825e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 3.6089e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 9.4947e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.00049588
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.00013046
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00018327
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 4.8218e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 2.6182e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 6.8883e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00015709
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 4.133e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.0021585
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.0005679
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 4.7057e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.238e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 6.7224e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.7686e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 4.0334e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 1.0612e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.00055422
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.00014581
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 4.9533e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.3032e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 7.0762e-07
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.8617e-07
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | grow into | 4.2457e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | grow into | 1.117e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | grow into | 5.8339e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | grow into | 1.5349e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00024767
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 6.516e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 3.5381e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 9.3085e-06
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00021229
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 5.5851e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.002917
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.00076744
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | Contact from object | other contact from object | 0.00036171
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | Contact from object | other contact from object | 0.0001033
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | Contact from object | other contact from object | 0.00046096
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | Contact from object | other contact from object | 5.1673e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | Contact from object | other contact from object | 1.4757e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | Contact from object | other contact from object | 6.5852e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | Contact from object | other contact from object | 0.00031004
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | Contact from object | other contact from object | 8.8542e-05
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | Contact from object | other contact from object | 0.00039511
HFTD - Transmission | HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | Contact from object | other contact from object | 0.0042602
HFTD - Transmission | HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | Contact from object | other contact from object | 0.0012166
HFTD - Transmission | HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | Contact from object | other contact from object | 0.0054291
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | Equipment / facility failure | other equipment / facility failure | 0.00041236
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | Equipment / facility failure | other equipment / facility failure | 0.00010849
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | Equipment / facility failure | other equipment / facility failure | 0.00040512
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | Equipment / facility failure | other equipment / facility failure | 5.8909e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | Equipment / facility failure | other equipment / facility failure | 1.5499e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | Equipment / facility failure | other equipment / facility failure | 5.7874e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | Equipment / facility failure | other equipment / facility failure | 0.00035346
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | Equipment / facility failure | other equipment / facility failure | 9.2992e-05
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | Equipment / facility failure | other equipment / facility failure | 0.00034725
HFTD - Transmission | HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | Equipment / facility failure | other equipment / facility failure | 0.0048567
HFTD - Transmission | HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | Equipment / facility failure | other equipment / facility failure | 0.0012778
HFTD - Transmission | HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | Equipment / facility failure | other equipment / facility failure | 0.0047714
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | Contact from object | other contact from object | 4.3026e-06
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | Contact from object | other contact from object | 4.451e-07
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | Contact from object | other contact from object | 4.7477e-06
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | Contact from object | other contact from object | 1.2293e-06
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Destructive Fires | Contact from object | other contact from object | 1.2717e-07
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | Contact from object | other contact from object | 1.3565e-06
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | Contact from object | other contact from object | 5.532e-05
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Large Fires | Contact from object | other contact from object | 5.7227e-06
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | Contact from object | other contact from object | 6.1042e-05
non-HFTD - Transmission | non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | Contact from object | other contact from object | 0.0057201
non-HFTD - Transmission | non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Small Fires | Contact from object | other contact from object | 0.00059173
non-HFTD - Transmission | non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | Contact from object | other contact from object | 0.0063118
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.7114e-07
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.5406e-05
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.1059e-07
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.2881e-05
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.8766e-07
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00010089
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.0075e-08
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.4498e-05
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 1.105e-06
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.00022861
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 2.5313e-07
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 5.2369e-05
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 1.9211e-07
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 3.9746e-05
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 1.341e-06
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.00027743
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 2.393e-07
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 4.9509e-05
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 3.1319e-07
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 6.4796e-05
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 2.374e-06
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.00049115
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.112e-09
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.4606e-09
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.5726e-08
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.7961e-06
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.5865e-09
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.5328e-10
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.0398e-08
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.1091e-06
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.0224e-08
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.9212e-09
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.3145e-07
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.3592e-05
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.2883e-10
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.5109e-10
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.7992e-09
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.0304e-07
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 1.7451e-08
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 4.9861e-09
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 2.2437e-07
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 2.32e-05
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 4.9357e-09
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.4102e-09
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | dead | 6.346e-08
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | dead | 6.5617e-06
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.2916e-09
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 6.5474e-10
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 2.9463e-08
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 3.0465e-06
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 1.0224e-08
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 2.9212e-09
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 1.3145e-07
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 1.3592e-05
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 3.173e-09
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 9.0657e-10
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 4.0795e-08
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 4.2182e-06
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 5.4646e-09
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.5613e-09
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | grow into | 7.0259e-08
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | grow into | 7.2648e-06
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 4.4245e-08
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.2642e-08
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 5.6887e-07
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 5.8821e-05
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.7052e-09
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.7052e-09
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.1347e-08
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.8174e-06
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.5414e-09
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.5414e-09
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.2873e-08
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.9278e-06
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.9476e-08
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.9476e-08
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.7528e-07
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.0099e-05
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.141e-09
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.141e-09
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.0269e-08
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.7635e-06
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 5.0776e-08
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 5.0776e-08
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 4.5699e-07
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 7.8475e-05
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.072e-08
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.072e-08
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 1.8648e-07
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 3.2023e-05
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.1524e-08
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.1524e-08
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 1.9372e-07
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 3.3266e-05
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 1.396e-07
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.396e-07
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 1.2564e-06
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.00021575
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.8163e-08
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.8163e-08
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 2.5347e-07
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 4.3526e-05
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.4377e-09
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.4377e-09
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 2.1939e-08
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 3.7674e-06
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.2025e-07
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.2025e-07
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 1.0823e-06
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.00018585
HFTD - Substation | HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.5021e-08
HFTD - Substation | HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.2146e-08
HFTD - Substation | HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.2875e-08
HFTD - Substation | HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.0014e-06
HFTD - Substation | HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.6681e-08
HFTD - Substation | HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.0973e-09
HFTD - Substation | HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.8584e-08
HFTD - Substation | HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.6757e-07
HFTD - Substation | HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.1094e-07
HFTD - Substation | HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 5.8705e-08
HFTD - Substation | HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.5223e-07
HFTD - Substation | HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.8399e-06
HFTD - Substation | HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.417e-08
HFTD - Substation | HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.0243e-09
HFTD - Substation | HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.2146e-08
HFTD - Substation | HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.6689e-07
HFTD - Substation | HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 8.3604e-07
HFTD - Substation | HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 1.1943e-07
HFTD - Substation | HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 7.1661e-07
HFTD - Substation | HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 9.8467e-06
HFTD - Substation | HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 3.1174e-07
HFTD - Substation | HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | dead | 4.4535e-08
HFTD - Substation | HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | dead | 2.6721e-07
HFTD - Substation | HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | dead | 3.6717e-06
HFTD - Substation | HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.4089e-07
HFTD - Substation | HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.4413e-08
HFTD - Substation | HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 2.0648e-07
HFTD - Substation | HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 2.8372e-06
HFTD - Substation | HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 1.0486e-06
HFTD - Substation | HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.498e-07
HFTD - Substation | HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 8.988e-07
HFTD - Substation | HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 1.235e-05
HFTD - Substation | HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.6923e-07
HFTD - Substation | HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 3.8462e-08
HFTD - Substation | HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 2.3077e-07
HFTD - Substation | HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 3.171e-06
HFTD - Substation | HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.834e-08
HFTD - Substation | HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 4.0486e-09
HFTD - Substation | HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | grow into | 2.4292e-08
HFTD - Substation | HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | grow into | 3.3379e-07
HFTD - Substation | HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.417e-06
HFTD - Substation | HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 2.0243e-07
HFTD - Substation | HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 1.2146e-06
HFTD - Substation | HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 1.6689e-05
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.2949e-05
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.6998e-06
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00016649
non-HFTD - Substation | non-HFTD - Substation | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.017215
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0015197
non-HFTD - Substation | non-HFTD - Substation | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.31442
HFTD - Substation | HFTD - Substation | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0011127
HFTD - Substation | HFTD - Substation | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00015895
HFTD - Substation | HFTD - Substation | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00095372
HFTD - Substation | HFTD - Substation | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.013105
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 9.7229e-05
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 9.7229e-05
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00087506
HFTD - Substation | HFTD - Substation | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.15027

## Match esc definition
Define a Customer Extrapolation Multiplier
match | x_match | matching with other series | y[i, j]= y[i-1, j] * x_match[i]/x_match[i-1]
x_match | Description | Year1 | Year2 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121
case1 |  | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Data & Validation
Lookup tables
No. | A | B | C | Risk/Cross Cutting Factor Name | RISK ID | Program Cost Options
1 | 0% | 10% | 15% | Aviation Incident | AVATN | prorate by Program Exposure
2 | 0% | 10% | 15% | Electric Transmission System-Wide Blackout | BLKOT | % of Total Cost (specify to the right)
3 | 0% | 10% | 15% | Loss of Containment on Gas Customer Connected Equipment | CCEPQ
4 | 0% | 2.5% | 5% | Climate | CLIMT | Program Exposure Options
5 | 0% | 2.5% | 5% | Loss of Containment on CNG Station Equipment | CNGEQ | Exposure unit
6 | 0% | 2.5% | 5% | Contractor Safety Incident | CNTSI | % of tranche exposure
7 | 0% | 2.5% | 5% | Insufficient Capacity to Meet High Demand | CPCTY | Work unit
8 | 0% | 2.5% | 5% | Contract Management | CTMGT
9 | 0% | 2.5% | 5% | Cyber Attack | CYBER | Program Type Options
10 | 0% | 2.5% | 5% | Failure of Electric Distribution Network Assets | DNTWK | Mitigation
11 | 0% | 2.5% | 5% | Failure of Electric Distribution Overhead Assets | DOVHD | Control
12 | 0% | 2.5% | 5% | Data Loss Event | DTALS | Foundational Mitigation
13 | 0% | 2.5% | 5% | Failure of Electric Distribution Underground Assets | DUNGD | Foundational Control
|  |  |  | Business Model - Electric | EMODL
|  |  |  | Employee Safety Incident | EMPSI
|  |  |  | Emergency Preparedness and Response | EPNDR
|  |  |  | Business Model - Gas | GMODL | Consequence Options
|  |  |  | Extended Unplanned Shutdown of a Critical Power Generation Asset | GSHUT | Safety
|  |  |  | Hazardous Material Release | HZMAT | Electric Reliability
|  |  |  | IT Asset Failure | ITAFL | Gas Reliability
|  |  |  | Large Uncontrolled Water Release (Dam Failure) | LGUWR | Financial
|  |  |  | Loss of Containment on LNG/CNG Portable Equipment | LNCNG
|  |  |  | Loss of Containment on Gas Distribution Main or Service | LOCDM | Bow Tie Element
|  |  |  | Loss of Containment on Gas Transmission Pipeline | LOCTR | LOF
|  |  |  | Liquidity Shortage | LQDTY | COF
|  |  |  | Large Overpressure Event Downstream of Gas Measurement and Control Facility | LRGOP | LOF and COF
|  |  |  | Loss of Containment at Gas Measurement and Control or Compression and Processing Facility | MCCPF
|  |  |  | Motor Vehicle Safety Incident | MTRSI
|  |  |  | Nuclear Core Damaging Event | NCORE
|  |  |  | Loss of Containment at Natural Gas Storage Well or Reservoir | NGSWR
|  |  |  | Nuclear Extended Shutdown | NSHUT
|  |  |  | Physical Attack | PHYSA
|  |  |  | Records and Information Management | RECIM
|  |  |  | Real Estate and Facilities Failure | REFFL
|  |  |  | Failure of Substation Assets | SBSTN
|  |  |  | Skilled and Qualified Workforce | SQWKF
|  |  |  | Seismic | SSMIC
|  |  |  | 3rd-Party Safety Incident | TPTSI
|  |  |  | Third-Party Risk | TRDPY
|  |  |  | Failure of Electric Transmission Overhead Assets | TRNHD
|  |  |  | Failure of Electric Transmission Underground Assets | TUNGD
|  |  |  | Wildfire | WLDFR

## BowTie
TableDriverSubdriver |  | TableTranche |  |  | TableOutcome
Driver | Subdriver | Tranche | Exposure | Unit | Outcome
Contact from object | Animal contact | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | 170.7528 | Miles | Red Flag Warning - Catastrophic Fires
Contact from object | Balloon contact | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | 306.602 | Miles | Red Flag Warning - Destructive Fires
Contact from object | Other contact from object | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | 1086.8999 | Miles | Red Flag Warning - Large Fires
Contact from object | Vehicle contact | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | 1434.2134 | Miles | Red Flag Warning - Small Fires
Vegetation Contact | Branch (Not overhanging, > 12ft) | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | 1628.5067 | Miles | Non-Red Flag Warning - Catastrophic Fires
Vegetation Contact | Branch (Not overhanging, 4-12ft) | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | 186.3964 | Miles | Non-Red Flag Warning - Destructive Fires
Vegetation Contact | Branch (Not overhanging, Distance Unknown) | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | 501.7453 | Miles | Non-Red Flag Warning - Large Fires
Vegetation Contact | Branch (Not overhanging, within 4ft) | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | 948.5456 | Miles | Non-Red Flag Warning - Small Fires
Vegetation Contact | Branch (OverHanging) | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | 1130.0763 | Miles | Seismic - Red Flag Warning - Catastrophic Fires
Vegetation Contact | Dead | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | 1453.2434 | Miles | Seismic - Non-Red Flag Warning - Catastrophic Fires
Vegetation Contact | Fell into (Moderate-Severe defect) | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | 500.9897 | Miles
Vegetation Contact | Fell into (No defect) | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | 714.3308 | Miles
Vegetation Contact | Fell into (slight defect) | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | 808.5801 | Miles
Vegetation Contact | Grow Into | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | 758.7044 | Miles
Vegetation Contact | Other/Unknown | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | 746.7011 | Miles
Contamination | Contamination | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | 692.6276 | Miles
Equipment / facility failure | Anchor / guy damage or failure | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | 574.6424 | Miles
Equipment / facility failure | Capacitor bank damage or failure | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | 749.2523 | Miles
Equipment / facility failure | Conductor damage or failure | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | 690.0576 | Miles
Equipment / facility failure | Connection device damage or failure | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | 489.3555 | Miles
Equipment / facility failure | Crossarm damage or failure | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | 700.8825 | Miles
Equipment / facility failure | Fuse damage or failure | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | 774.3498 | Miles
Equipment / facility failure | Insulator and brushing damage or failure | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | 487.9227 | Miles
Equipment / facility failure | Lightning arrestor damage or failure | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | 375.6459 | Miles
Equipment / facility failure | Other equipment / facility failure | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | 415.2775 | Miles
Equipment / facility failure | Pole damage or failure | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | 68.3395 | Miles
Equipment / facility failure | Recloser damage or failure | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | 145.2608 | Miles
Equipment / facility failure | Sectionalizer damage or failure | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | 57.5921 | Miles
Equipment / facility failure | Switch damage or failure | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | 88.5056 | Miles
Equipment / facility failure | Transformer damage or failure | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | 88.4245 | Miles
Equipment / facility failure | Voltage regulator / booster damage or failure | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | 226.4749 | Miles
Other | All Other | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | 280.2309 | Miles
Unknown | Unknown | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | 267.1271 | Miles
Vandalism / Theft | Vandalism / Theft | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | 69.0654 | Miles
Wire-to-wire contact | Wire-to-wire contact / contamination | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | 33.5215 | Miles
Utility work / Operation | Utility work / Operation | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | 459.7243 | Miles
CC - Seismic Scenario | Seismic Scenario | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | 610.7187 | Miles
|  | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | 206.7005 | Miles
|  | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | 208.0009 | Miles
|  | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | 90.0882 | Miles
|  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | 655.3922 | Miles
|  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | 572.4174 | Miles
|  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | 334.8643 | Miles
|  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | 248.6831 | Miles
|  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | 73.245 | Miles
|  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | 1419.6506 | Miles
|  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | 612.5567 | Miles
|  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | 143.628 | Miles
|  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | 84.7422 | Miles
|  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | 79.7972 | Miles
|  | HFTD - Distribution - Zone 1 - 1QU CoRE ¦ 5QU LoRE | 0.18783 | Miles
|  | HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | 0.13442 | Miles
|  | HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | 10.0154 | Miles
|  | HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | 0.27822 | Miles
|  | HFTD - Substation | 1 | Unit
|  | HFTD - Transmission - Tier 2 - 115 kV or Lower | 1299.3 | Miles
|  | HFTD - Transmission - Tier 2 - 230 kV or Higher | 1759.53 | Miles
|  | HFTD - Transmission - Tier 2 - 60/70 kV | 1419.51 | Miles
|  | HFTD - Transmission - Tier 3 - 115 kV or Lower | 446.95 | Miles
|  | HFTD - Transmission - Tier 3 - 230 kV or Higher | 557.6 | Miles
|  | HFTD - Transmission - Tier 3 - 60/70 kV | 376.43 | Miles
|  | HFTD - Transmission - Zone 1 - 115 kV or Lower | 1.27 | Miles
|  | HFTD - Transmission - Zone 1 - 230 kV or Higher | 3.1 | Miles
|  | HFTD - Transmission - Zone 1 - 60/70 kV | 1.8 | Miles
|  | non-HFTD - Distribution | 55300 | Miles
|  | non-HFTD - Substation | 1 | Unit
|  | non-HFTD - Transmission - 115 kV or Lower | 4431.1 | Miles
|  | non-HFTD - Transmission - 230 kV or Higher | 5106.55 | Miles
|  | non-HFTD - Transmission - 60/70 kV | 3682.86 | Miles
|  | HFTD - Distribution - Zone 1 - All | 10.6159 | Miles
|  | HFTD - Distribution - Tier 2 - All | 18326.3019 | Miles
|  | HFTD - Distribution - Tier 3 - All | 7124.7516 | Miles
|  | HFTD - Distribution - All | 25461.6694 | Miles
|  | HFTD - Transmission - All | 5865.49 | Miles
|  | HFTD - All | 31327.1594 | Miles
|  | non-HFTD - Transmission - All | 13220.51 | Miles
|  | HFTD - Transmission - Tier 3 - All | 1380.98 | Miles
|  | HFTD - Transmission - Tier 2 - All | 4478.34 | Miles
|  | HFTD - Transmission - Zone 1 - All | 6.17 | Miles
|  | non-HFTD - Transmission - All | 13220.51 | Miles
|  | All | 99847.6694 | Miles

## HFTD Miles
HFTD Line Miles | 25461.6694
| HFTD Tranche % based on WMP BowTie | Line Miles
Zone 1 | 0.06% | 15.277
Tier 3 | 27.93% | 7111.4443
Tier 2 | 72.01% | 18334.9481

## TablePVRR
Asset Group | PVRR Multiplier (no O&M) | Lifetime O&M as % of PVRR
Buildings | 1.4702 | 0
Communications equipment | 1.2527 | 0
Computer hardware | 1.1238 | 0.44918
Computer software | 1.1074 | 0.44918
Electric distribution (<69kV) - Overhead | 1.3891 | 1.1158
Electric distribution (<69kV) - Underground | 1.3891 | 0.38678
Electric transmission (69kV+) | 1.3758 | 0
Electric smart meter | 1.229 | 0
Gas distribution after 2010 | 1.4002 | 1.1518
Gas Meters | 1.3726 | 7.7616
Gas transmission & storage | 1.3686 | 1.7862
Gas (current) held for resale | 1.5881 | 0
Land easement | 1.5197 | 0
Land purchase | 1.448 | 0
Motor vehicles | 1.1661 | 0
Office furniture | 1.241 | 0
Hydro | 1.405 | 0
Hydro additions | 1.3416 | 0
Nuclear | 1.2779 | 0
Nuclear additions | 1.1917 | 0
Fuel cell | 1.1589 | 0
Custom | 0 | 0